## WTG Yield Wake
WTG 1
Diameter |  | 280 | m
Swept area |  | 61575.216 | m^2
Rated power |  | 20 | MW
Power density rotor |  | 324.806 | W/m^2
Rated rotor speed |  | 7 | rpm
Rated tip speed |  | 102.6254 | m/s
Hub height |  | 160 | m
# of WTGs:
WTG 1 Parameters*) |  |  |  |  | Offshore Site 1 |  |  | 80
Wind speed | Power in the Wind | WTG Power | C_P | C_T | Free windspeed at hub height | Time | Gross Yield | Park Efficiency | Gross Yield incl. Wake Loss
(m/s) | (MW) | (MW) |  |  | (m/s) | % of year | (MWh/year) | % | (MWh/year)
0.5 | 0.0047105 | 0 | 0 | 0 | 0.5 | 0.652 | 0
1.5 | 0.12718 | 0 | 0 | 0 | 1.5 | 1.735 | 0
2.5 | 0.58881 | 0 | 0 | 0 | 2.5 | 3.356 | 0
3.5 | 1.6157 | 0.437 | 0.27047 | 0.855 | 3.5 | 4.832 | 185.1015 | 48.94% | 7246.525
4.5 | 3.434 | 1.423 | 0.41439 | 0.855 | 4.5 | 6.39 | 797.0898 | 56.66% | 36132.9691
5.5 | 6.2697 | 2.83 | 0.45138 | 0.855 | 5.5 | 7.657 | 1899.5317 | 61.63% | 93659.2279
6.5 | 10.349 | 4.772 | 0.46111 | 0.858 | 6.5 | 8.732 | 3652.7137 | 63.67% | 186041.2062
7.5 | 15.898 | 7.46 | 0.46924 | 0.863 | 7.5 | 9.448 | 6178.4591 | 64.58% | 319182.8734
8.5 | 23.1427 | 10.949 | 0.47311 | 0.84 | 8.5 | 9.619 | 9232.2137 | 66.2% | 488953.4761
9.5 | 32.3093 | 14.623 | 0.45259 | 0.752 | 9.5 | 9.123 | 11694.3374 | 69.86% | 653553.437
10.5 | 43.624 | 17.73 | 0.40643 | 0.641 | 10.5 | 8.192 | 12732.1031 | 75.62% | 770256.4134
11.5 | 57.3127 | 19.442 | 0.33923 | 0.521 | 11.5 | 7.082 | 12069.7515 | 83.77% | 808849.1604
12.5 | 73.6016 | 19.921 | 0.27066 | 0.402 | 12.5 | 5.825 | 10172.0511 | 91.79% | 746939.7361
13.5 | 92.7169 | 19.991 | 0.21561 | 0.309 | 13.5 | 4.558 | 7987.4896 | 96.66% | 617663.6709
14.5 | 114.8845 | 20 | 0.17409 | 0.244 | 14.5 | 3.373 | 5913.5436 | 99.18% | 469192.0147
15.5 | 140.3306 | 20 | 0.14252 | 0.197 | 15.5 | 2.414 | 4232.2248 | 99.94% | 338385.1175
16.5 | 169.2814 | 20 | 0.11815 | 0.162 | 16.5 | 1.801 | 3157.5132 | 99.94% | 252457.1651
17.5 | 201.9629 | 20 | 0.099028 | 0.136 | 17.5 | 1.415 | 2480.778 | 99.94% | 198349.1886
18.5 | 238.6012 | 20 | 0.083822 | 0.116 | 18.5 | 1.146 | 2009.1672 | 99.94% | 160641.8164
19.5 | 279.4224 | 20 | 0.071576 | 0.1 | 19.5 | 0.864 | 1514.7648 | 99.94% | 121112.1547
20.5 | 324.6526 | 20 | 0.061604 | 0.088 | 20.5 | 0.612 | 1072.9584 | 99.94% | 85787.7763
21.5 | 374.518 | 20 | 0.053402 | 0.078 | 21.5 | 0.435 | 762.642 | 99.94% | 60976.6057
22.5 | 429.2447 | 20 | 0.046593 | 0.07 | 22.5 | 0.294 | 515.4408 | 99.94% | 41211.7749
23.5 | 489.0587 | 18.4 | 0.037623 | 0.058 | 23.5 | 0.181 | 291.9429 | 104% | 24289.6463
24.5 | 554.1861 | 15.2 | 0.027428 | 0.044 | 24.5 | 0.109 | 145.2351 | 104% | 12083.5593
25.5 | 624.8531 | 12 | 0.019205 | 0.033 | 25.5 | 0.071 | 74.6863 | 104% | 6213.9018
26.5 | 701.2857 | 8.8 | 0.012548 | 0.023 | 26.5 | 0.039 | 30.0849 | 104% | 2503.0647
27.5 | 783.7101 | 5.6 | 0.0071455 | 0.0015 | 27.5 | 0.027 | 13.2542 | 104% | 1102.7488
28.5 | 872.3524 | 0 | 0 | 0 | 28.5 | 0.018 | 0 | 0% | 0
*) C_P provided here is assumed to include all WTG aerodynamic, drive train and internal electrical losses. | [6 empty] | 98815.0782 |  | 6502785.2305 | MWh/year
[7 empty] | WTG |  | Park
[6 empty] | Capacity Factor | 56.4% |  | 46.4%

## IAC
Cable 1 |  |  | 400 mm2 | 0.101 | Ohm/km
Cable 2 |  |  | 630 mm2 | 0.063 | Ohm/km
Cable 3 |  |  | 800 mm2 | 0.037 | Ohm/km
|  |  | WTG 1 | WTG 2 | WTG 3 | WTG 4
WTG Nominal Power [MVA] |  |  | 21.1 | 21.1 | 21.1 | 21.1
IAC Voltage kV |  |  | 66 | 66 | 66 | 66
# WTGs on IAC Section |  |  | 1 | 2 | 3 | 4
Nominal Current [A] on IAC Section
IAC Section Cable 1 / 2 / 3
Resistance [Ohm/km]
|  |  | km | km | km | km
String Section Length [km] |  |  | 2.5 | 2.5 | 2 | 1.5
Free Wind Speed | Power | [5 empty] | P_loss | hours | Loss
(m/s) | MW | MVA |  |  |  |  | [kW] |  | [MWh/year]
0.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 57 | 0
1.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 151.986 | 0
2.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 293.9856 | 0
3.5 | 0.437 |  | 0 | 0 | 0 | 0 | 0 | 423.2832 | 0
4.5 | 1.423 |  | 0 | 0 | 0 | 0 | 0 | 559.764 | 0
5.5 | 2.83 |  | 0 | 0 | 0 | 0 | 0 | 670.7532 | 0
6.5 | 4.772 |  | 0 | 0 | 0 | 0 | 0 | 764.9232 | 0
7.5 | 7.46 |  | 0 | 0 | 0 | 0 | 0 | 827.6448 | 0
8.5 | 10.949 |  | 0 | 0 | 0 | 0 | 0 | 842.6244 | 0
9.5 | 14.623 |  | 0 | 0 | 0 | 0 | 0 | 799.1748 | 0
10.5 | 17.73 |  | 0 | 0 | 0 | 0 | 0 | 717.6192 | 0
11.5 | 19.442 |  | 0 | 0 | 0 | 0 | 0 | 620.3832 | 0
12.5 | 19.921 |  | 0 | 0 | 0 | 0 | 0 | 510.27 | 0
13.5 | 19.991 |  | 0 | 0 | 0 | 0 | 0 | 399.2808 | 0
14.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 295.4748 | 0
15.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 211.4664 | 0
16.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 157.7676 | 0
17.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 123.954 | 0
18.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 100.3896 | 0
19.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 75.6864 | 0
20.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 53.6112 | 0
21.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 38.106 | 0
22.5 | 20 |  | 0 | 0 | 0 | 0 | 0 | 25.7544 | 0
23.5 | 18.4 |  | 0 | 0 | 0 | 0 | 0 | 15.8556 | 0
24.5 | 15.2 |  | 0 | 0 | 0 | 0 | 0 | 9.5484 | 0
25.5 | 12 |  | 0 | 0 | 0 | 0 | 0 | 6.2196 | 0
26.5 | 8.8 |  | 0 | 0 | 0 | 0 | 0 | 3.4164 | 0
27.5 | 5.6 |  | 0 | 0 | 0 | 0 | 0 | 2.3652 | 0
28.5 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 0
[8 empty] | 8759.308 |  | h/year
IAC String Losses (MWh/year) | [8 empty] | 0 | MWh/year
WTG Energy Yield (MWh/year) | [9 empty] | MWh/year
Losses (% WTG Energy Yield/year) | [9 empty] | /year